# NIMechE Refrigeration Systems Principles & Design

## Assignment 2:

## Eniola Enijeshiku

## eenijeshiku@gmail.com

### Part A – Design Basis

Determine:

- Room temperature = 35F

- SST = Room Temperature – Evaporator TD

= 35F – 10F= 25F

- Ambient temperature = 90F

- CDT = Ambient Temperature + Condenser TD = 90F – 15F = 105F

- Room Load

= 1MBH = 1000BTU/Hr

24 MBH = 24,000 BTU/Hr

1Ton = 12, 000 BTU/Hr

24,000/12,000 = 2 Ton of refrigeration

### Part B – Equipment Selection

Research and recommend:

- Compressor manufacturer and model

Answer: -

Manufacturer: BITZER

Model: 2FES-2Y-4SU

Basis of Selection:

Using BITZER Software, a compressor was selected for R448A refrigerant at an evaporating temperature of 25°F and condensing temperature of 105°F. The selected compressor model 2FES-2Y-4SU provides a cooling capacity of 27.4 kBTU/hr, which exceeds the required design load of 24 kBTU/hr. Therefore, it is suitable for the refrigeration system.

- Evaporator manufacturer and model

Answer: - The evaporator should provide approximately: 24,000 BTU/Hr

One example is:

### Evaporator Manufacturer: Patton

Model: JMC230 Unit Cooler

Capacity with R-448A is approximately 22,980 W, which is far above the required 24,000 BTU/hr (≈7,030 W), giving adequate capacity for the application.

 Medium-temperature cooler application

 Capacity exceeds required load

 Air-defrost operation is suitable for a 35°F cooler.

- Air-cooled condenser manufacturer and model

Answer: - An air-cooled condenser rated around 30,000 BTU/hr at 105°F CDT.

Manufacturer: Heatcraft

Model: Bohn OACH Series Air-Cooled Condenser (≈30,000 BTU/hr capacity)

- Air-cooled design

- Capacity exceeds heat rejection requirement

- Suitable for 90°F ambient conditions

- Compatible with R-448A refrigeration systems

- Liquid receiver size:  For a system of approximately 2 tons using R448A, 1.5–2-gallon receiver is typically appropriate.

Basis: Suitable refrigerant storage capacity for a 2-ton R-448A refrigeration system.

 Store excess refrigerant during pump-down

 Accommodate seasonal refrigerant variations

 Ensure a solid liquid column reaches the expansion valve

### Part C – Piping Design

Provide recommendations for:

- Suction line

- Liquid line

- Discharge line

Discuss:

- Pressure drop considerations

- Oil return considerations

- Insulation requirements

ANSWER: -

State the basis for your selections.